Summary of 1000X1000 Ceiling Access Hatch tested to 2 Hours

- 13mmx100mmx0.9mm thick rear protection plates running the perimeter of the megadeco board.

- LSP90 6mmx8mm Poly Urethane polyester air seal to all closing sides of frame and mullion.

- 1000X1000x1.2mm thick Zintec frame 65mm deep with 20mm closing edge for mounting air seal.

- 896x896x49mm deep x 0.9mm thick door leaf.

- 16mm Plastic bung to close lock hole off.

- 20x48x100x48mm 0.9mm thick top hats in rear of door tray to support board.

- 12.5mm thick Megadeco screw fixed to rear of door tray painted with Lafarge drywall sealer /10l ref 2760736 BS476 Part 4 1968

- 1.5mm thick Gold and Wassell 1628S piano hinge bolted to access panel frame with M6 bolts, nuts and penny washers

- 3 way locking system on door engaging through the frame sides.